## GENNAIO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-01-18 | pH | INLET | SINGLE GRAB | YES | YES | 7.5
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 6
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.04
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.04
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.7
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 14
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 16
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.27
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.2
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.06

## FEBBRAIO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-02-21 | pH | INLET | SINGLE GRAB | YES | YES | 7.7
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 8
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 2
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.13
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 2.8
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 18
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 7
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 16
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.21
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.8
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09

## MARZO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-03-21 | pH | INLET | SINGLE GRAB | YES | YES | 7.7
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 12
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 3
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.19
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 2.8
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.05
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.7
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 14
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 14
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.28
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.5
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.08

## APRILE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-04-19 | pH | INLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 9
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 4
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.16
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 2.7
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.06
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.75
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 19
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 17
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.5
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.08

## MAGGIO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-05-23 | pH | INLET | SINGLE GRAB | YES | YES | 7.7
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 5
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.16
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 3.2
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.02
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.5
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 17
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 15
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.26
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.6
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09

## GIUGNO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-06-20 | pH | INLET | SINGLE GRAB | YES | YES | 7.55
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 8
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 4
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.17
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 3.6
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.06
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 16
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 20
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.24
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.6
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09

## LUGLIO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-07-20 | pH | INLET | SINGLE GRAB | YES | YES | 7.7
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 12
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 4
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.22
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 3.5
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.04
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.7
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 23
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 8
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 22
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.26
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.5
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09

## AGOSTO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-08-29 | pH | INLET | SINGLE GRAB | YES | YES | 7.7
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 15
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 4
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.19
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 3.6
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.08
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.59
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 26
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 8
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 24
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.26
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.8
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09

## SETTEMBRE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-09-21 | pH | INLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 11
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 3
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.15
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 3.6
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.04
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 15
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 4
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 15
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.23
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.7
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09

## OTTOBRE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-10-19 | pH | INLET | SINGLE GRAB | YES | YES | 7.65
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 5
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.16
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 3.8
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.04
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 18
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 4
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 16
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.23
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.9
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.06

## NOVEMBRE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-11-21 | pH | INLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 4
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 2
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.16
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 3.8
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.05
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 18
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 19
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.28
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6.6
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09

## DICEMBRE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2022-12-19 | pH | INLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 4
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.19
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.03
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 19
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 18
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.2
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.25
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6.3
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.08

## SATURAZIONE OSSIGENO
ACQUA IN USCITA VASCHE ALLEVAMENTO
MESE | DATA RILEVAZIONE | OSSIGENO DISCIOLTO [mg/l] | TEMPERATURA | PRESSIONE [mmHg] | VALORE SATURAZIONE DI O2 [mg/l] | SATURAZIONE PERCENTUALE [%]
GENNAIO | 2022-01-18 | 10 | 10.8 | 751.12 | 11.2792 | 88.6588
FEBBRAIO | 2022-02-18 | 9.9 | 10.9 | 751.12 | 11.3057 | 87.5662
MARZO | 2022-03-17 | 10.1 | 11.1 | 751.12 | 11.2532 | 89.7522
APRILE | 2022-04-20 | 10 | 11.5 | 751.12 | 10.2792 | 97.2838
MAGGIO | 2022-05-18 | 9.8 | 11.8 | 751.12 | 11.3323 | 86.4788
GIUGNO | 2022-06-20 | 9.7 | 12 | 751.12 | 11.3588 | 85.3965
LUGLIO | 2022-07-20 | 9.7 | 11.9 | 751.12 | 11.3588 | 85.3965
AGOSTO | 2022-08-29 | 9.5 | 12.8 | 751.12 | 11.4118 | 83.2469
SETTEMBRE | 2022-09-21 | 9.8 | 11.9 | 751.12 | 11.3323 | 86.4788
OTTOBRE | 2022-10-19 | 10.1 | 11.5 | 751.12 | 11.2532 | 89.7522
NOVEMBRE | 2022-11-21 | 9.9 | 10.8 | 751.12 | 11.3057 | 87.5662
DICEMBRE | 2022-12-19 | 10 | 10.2 | 751.12 | 10.2792 | 97.2838
La % di saturazione di OD (concentrazione di ossigeno disciolto; in inglese DO) è data dal rapporto, in % appunto, tra l'effettiva quantità di OD e il massimo valore possibile in funzione della temperatura e dell'altitudine.
Altitudine TORRE= 95m.
Pressione in funzione dell'altitudine: p= 0,9877q; dove P=pressione in atm - q=altitudine in centinaia di metri (nel caso di TORRE q=0,95), da cui p=0,988311atm (751,12mm di Hg)
Dalla Tabella allegata si ottengono i valori di saturazione di O2 con interpolazione lineare dei dati in funzione della temperatura e della pressione
| °C | 760mm | 750mm | 751,12mm | valore saturazione (output)
temperatura più bassa | 9 | 11.62 | 11.46 | 11.5445 | 11.4118
temperatura più alta | 10 | 11.35 | 11.2 | 11.2792
temperatura rilevata (imput) | 9.5
temperatura più bassa | 10 | 11.35 | 11.2 | 11.2792 | 11.2792
temperatura più alta | 11 | 11.09 | 10.94 | 11.0192
temperatura rilevata (imput) | 10
temperatura più bassa | 11 | 11.09 | 10.94 | 11.0192 | 10.872
temperatura più alta | 12 | 10.84 | 10.7 | 10.7739
temperatura rilevata (imput) | 11.6
temperatura più bassa | 12 | 10.84 | 10.7 | 10.7739 | 10.7739
temperatura più alta | 13 | 10.6 | 10.46 | 10.5339
temperatura rilevata (imput) | 12