## GENNAIO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-01-16 | pH | INLET | SINGLE GRAB | YES | YES | 7.51
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.6
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 7
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## FEBBRAIO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-02-18 | pH | INLET | SINGLE GRAB | YES | YES | 7.5
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.5
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 8
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.07
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.5
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## MARZO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2019-03-11 | pH | INLET | SINGLE GRAB | YES | YES | 7.5
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.6
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.55
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.11
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.6
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## APRILE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-04-20 | pH | INLET | SINGLE GRAB | YES | YES | 7.53
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.6
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.58
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.3
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## MAGGIO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-05-18 | pH | INLET | SINGLE GRAB | YES | YES | 7.6
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.5
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.45
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 8
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.9
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## GIUGNO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-06-16 | pH | INLET | SINGLE GRAB | YES | YES | 7.52
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.8
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.58
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 9
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.12
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.8
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## LUGLIO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-07-14 | pH | INLET | SINGLE GRAB | YES | YES | 7.55
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.9
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 763
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 9
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.12
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.9
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## AGOSTO
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-08-13 | pH | INLET | SINGLE GRAB | YES | YES | 7.63
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 4
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.04
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.9
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.52
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 8
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.14
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.7
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## SETTEMBRE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-09-17 | pH | INLET | SINGLE GRAB | YES | YES | 7.55
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.6
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.58
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 9
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.13
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## OTTOBRE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-10-15 | pH | INLET | SINGLE GRAB | YES | YES | 7.52
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.8
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.55
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.7
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## NOVEMBRE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-11-16 | pH | INLET | SINGLE GRAB | YES | YES | 7.56
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.7
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.54
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.09
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 5.9
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## DICEMBRE
DATE | ANALYSIS | LOCATION | METHOD | SAMPLING BY THIRD PARTY? | ANALYSIS BY THIRD PARTY? | RESULT
2020-12-16 | pH | INLET | SINGLE GRAB | YES | YES | 7.53
| SOS (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| BOD (mg/l) | INLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | INLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| N nitrico (mg/l) | INLET | SINGLE GRAB | YES | YES | 4.8
| P tot (mg/l) | INLET | SINGLE GRAB | YES | YES | 0.01
| pH | OUTLET | SINGLE GRAB | YES | YES | 7.5
| SOS (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 4
| BOD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 1
| COD (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 10
| N amm (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.1
| N nitroso (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.03
| N nitrico (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 6
| P tot (mg/l) | OUTLET | SINGLE GRAB | YES | YES | 0.01

## SATURAZIONE OSSIGENO
ACQUA IN USCITA VASCHE ALLEVAMENTO
MESE | DATA RILEVAZIONE | OSSIGENO DISCIOLTO [mg/l] | TEMPERATURA | PRESSIONE [mmHg] | VALORE SATURAZIONE DI O2 [mg/l] | SATURAZIONE PERCENTUALE [%]
GENNAIO | 2020-01-16 | 10.5 | 9.8 | 748.52 | 11.0594 | 94.9422
FEBBRAIO | 2020-02-18 | 10.5 | 9.5 | 748.52 | 11.1494 | 94.1758
MARZO | 2020-03-17 | 10.3 | 9.8 | 748.52 | 11.0594 | 93.1338
APRILE | 2020-04-20 | 10.1 | 10.1 | 748.52 | 11.0953 | 91.0293
MAGGIO | 2020-05-18 | 9.9 | 10.6 | 748.52 | 10.968 | 90.2628
GIUGNO | 2020-06-16 | 9.8 | 11.1 | 748.52 | 10.8421 | 90.3886
LUGLIO | 2020-07-14 | 9.7 | 11.4 | 748.52 | 10.7701 | 90.0643
AGOSTO | 2020-08-13 | 9.7 | 12 | 748.52 | 10.6261 | 91.2848
SETTEMBRE | 2020-09-17 | 9.7 | 11.9 | 748.52 | 10.6501 | 91.0791
OTTOBRE | 2020-10-15 | 10 | 11.1 | 748.52 | 10.8421 | 92.2332
NOVEMBRE | 2020-11-16 | 10.1 | 10.6 | 748.52 | 10.968 | 92.0863
DICEMBRE | 2020-12-16 | 10.3 | 10.3 | 748.52 | 11.0444 | 93.2601
La % di saturazione di OD (concentrazione di ossigeno disciolto; in inglese DO) è data dal rapporto, in % appunto, tra l'effettiva quantità di OD e il massimo valore possibile in funzione della temperatura e dell'altitudine.
Altitudine CALCIO= 123m.
Pressione in funzione dell'altitudine: p= 0,9877q; dove P=pressione in atm - q=altitudine in centinaia di metri (nel caso di CALCIO q=1,23), da cui p=0,984892atm (748,52mm di Hg)
Dalla Tabella allegata si ottengono i valori di saturazione di O2
| °C | 740mm | 750mm | 748,52mm | valore saturazione (output)
temperatura più bassa | 9 | 11.12 | 11.5 | 11.2994 | 11.0594
temperatura più alta | 10 | 10.82 | 11.2 | 10.9994
temperatura rilevata (input) | 9.8
temperatura più bassa | 10 | 11.05 | 11.2 | 11.1208 | 10.8151
temperatura più alta | 11 | 10.8 | 10.94 | 10.8661
temperatura rilevata (input) | 11.2
temperatura più bassa | 11 | 10.8 | 10.94 | 10.8661 | 10.6501
temperatura più alta | 12 | 10.56 | 10.7 | 10.6261
temperatura rilevata (input) | 11.9
temperatura più bassa | 12 | 10.56 | 10.7 | 10.6261 | 10.5061
temperatura più alta | 13 | 10.32 | 10.46 | 10.3861
temperatura rilevata (input) | 12.5